The purpose of this document is to summarize the major software and integration changes made from the original GitHub ARPO controller repository to the updated apro-controller-rev2 version.

- Inverter Timing and GPIO Improvements

- Separated inverter timing from blocking controller operations.

- Improved GPIO waveform stability during integrated operation.

- Added safer inverter interlock behavior.

- Improved startup and shutdown handling.

Example:

# Inverter startup

inv = InverterController()

inv.start()

# Inverter shutdown

inv.stop()

- Outage and Restore Transfer Logic

- Reduced outage detection latency.

- Added debounce logic to reduce nuisance transfers.

- Changed restore sequence to stop inverter before relay transfer.

- Improved relay timing stability.

Example:

# Restore sequence

inverter.stop()

time.sleep(0.25)

relay.switch_to_grid()

- ADC and RMS Measurement Improvements

- Integrated tested RMS voltage and current calculations.

- Added calibrated scaling constants.

- Reduced ADC sample count to improve response time.

- Fixed stale current display values.

Example:

# Grid current scaling

K_GRID_I = 2.9904

# Grid voltage scaling

K_GRID_V = 1055.5671

- Fast Outage Detection Changes

- Implemented fast outage voltage monitoring.

- Added separate display and trip logic handling.

- Improved transfer response timing.

Example:

# Fast outage logic

if values["grid_voltage"] < GRID_FAIL_VOLTAGE_AC:

start_backup_sequence()

- Logging and Timing Improvements

- Added software transfer timing measurements.

- Added improved console logging.

- Added more detailed status messages.

Example:

print(

f"[TIMING] SOFTWARE TRANSFER TIME = "

f"{transfer_time:.3f} seconds"

)

- ADC Calibration Tuning

- Added comments for future tuning.

- Separated voltage and current scaling factors.

- Improved calibration readability for future testing.

Example:

# Current calibration adjustment

# Increase if displayed current is too low.

K_GRID_I = 2.9904

# Voltage calibration adjustment

K_GRID_V = 1055.5671

There are remaining major issues such as inverter voltage sag under larger loads which is the result of loss across the MOSFET’s themselves. Software transfer timing, GPIO stability, relay control, and ADC sensing are now operating correctly during integrated testing. The voltage sag appears related to inverter and transformer hardware limitations rather than controller software.

Integrated Test Results

| Test | Observed Result |
| --- | --- |
| Utility to Backup Transfer | ~0.9 second software transfer |
| Backup to Utility Restore | ~0.8 second restore |
| GPIO Waveform Stability | Stable during integrated operation |
| Current Readings | Working correctly after ADC fixes |
| Fan Load Test | Successful |