Purpose:

This guide walks through setting up the Raspberry Pi, installing the ADC/LCD dependencies, placing the Rev2 controller folder, testing each hardware layer, and running the full ARPO integration controller. It assumes that you have a fresh Raspberry Pi setup where the project folder and Python dependencies have not been installed yet.

Rev2 Summary:

- The controller reads all four ADC channels every loop so voltage and current values on the terminal, LCD, and logs are real measured values.

- The inverter square wave runs in a separate process so ADC reads, LCD updates, and logging do not stretch the GPIO 23 and GPIO 24 waveform.

- GPIO 27 relay polarity is set for the tested DPDT relay module: HIGH selects grid and LOW selects backup.

- RMS voltage/current scaling is centralized in app_config/settings.py so you can tune calibration values without modifying the controller logic.

- Timestamped logs are saved in the logs folder for outage transfer time, restore time, voltage, current, mode, and relay status.

Hardware Assumptions:

| Item | Assumption |
| --- | --- |
| Controller | Raspberry Pi with GPIO access |
| ADC | Waveshare High-Precision AD HAT using ADS1263 |
| LCD | 16x2 I2C LCD with address 0x27 |
| Relay | GPIO 27 controls DPDT relay source selection |
| Inverter GPIO | GPIO 23 and GPIO 24 control H-bridge polarity |
| ADC channels | IN0 grid voltage, IN1 grid current, IN2 backup voltage, IN3 backup current |

Safety Notes Before Testing:

- For GPIO-only tests, disconnect MOSFET gates, transformer, load, and H-bridge battery power.

- Before powering the inverter hardware, force GPIO 23 LOW, GPIO 24 LOW, and GPIO 27 HIGH.

- Use an inline fuse and current-limited DC supply while testing the inverter stage.

- Stop immediately if DC current stays high, a MOSFET heats quickly, the transformer gets hot, or a fuse trips repeatedly.

- Keep GPIO_LOGIC_TEST_IGNORE_BACKUP_LOW set to True only during GPIO-only or incomplete inverter-output tests. Set it to False for final protection testing.

- Prepare Raspberry Pi Interfaces

Open Raspberry Pi configuration and enable I2C and SPI.

sudo raspi-config

Use Interface Options and enable I2C and SPI. Reboot after changing interface settings.

sudo reboot

After reboot, confirm the I2C LCD backpack is visible. The expected address from testing is 0x27.

i2cdetect -y 1

- Install System Packages

Install the packages needed for Python, I2C, and the LCD/ADC support.

sudo apt update sudo apt install -y python3-pip python3-smbus i2c-tools git

- Install Python Packages

From inside the project folder, install the Python package requirements.

cd /home/justin/Documents/apro-controller-rev2 pip3 install --break-system-packages -r requirements.txt

The setup script can also do this automatically:

cd /home/justin/Documents/apro-controller-rev2 chmod +x setup.sh run.sh ./setup.sh

- Install or Confirm ADS1263 Driver Folder

The controller expects the Waveshare ADS1263 Python driver folder at one of these paths:

/home/justin/High-Pricision_AD_HAT/python /home/justin/High-Precision_AD_HAT/python

If the folder is missing, copy or clone the Waveshare High-Precision AD HAT Python driver to the Pi. The important point is that the folder contains ADS1263.py. Confirm it with:

ls /home/justin/High-Pricision_AD_HAT/python/ADS1263.py

If the path is different, update ADC_DRIVER_PATH in app_config/settings.py.

- Place the Rev2 Project Folder

Copy the apro-controller-rev2 folder to the Pi. The expected path is:

/home/justin/Documents/apro-controller-rev2

From that folder, the main program is started as a Python module:

cd /home/justin/Documents/apro-controller-rev2 python3 -m src.main

- Confirm GPIO Safe States

Before connecting the inverter hardware, force the GPIO outputs into safe states.

sudo pinctrl set 23 op dl sudo pinctrl set 24 op dl sudo pinctrl set 27 op dh

Expected hardware state: GPIO 23 LOW and GPIO 24 LOW turns the inverter output off. GPIO 27 HIGH selects grid/utility on the DPDT relay.

- Test ADC Current and Voltage Readings

Run the current channel diagnostic with the grid load turned on. This verifies the repo ADC path, not just the standalone test file.

cd /home/justin/Documents/apro-controller-rev2 python3 -m scripts.current_channel_debug

Expected result with the tested load is IN1 grid current near the measured load current. During testing, this was approximately 0.8 A. IN3 should be near zero unless the backup source is supplying the load.

- Test the Inverter GPIO Process Only

Keep MOSFET gates, transformer, load, and H-bridge battery power disconnected. Scope GPIO 23 and GPIO 24. Then run:

cd /home/justin/Documents/apro-controller-rev2 python3 -m scripts.inverter_process_test

Expected result: GPIO 23 and GPIO 24 alternate cleanly and never go HIGH at the same time.

- Test Relay and Inverter GPIO Sequence

With the power stage still disconnected, run the sequence test. This checks GPIO 23, GPIO 24, and GPIO 27 sequencing without ADC or LCD logic involved.

cd /home/justin/Documents/apro-controller-rev2 python3 -m scripts.gpio_outage_sequence_test

Expected result: grid mode first, inverter GPIO switching during simulated backup, relay transfer to backup, inverter stop, and relay return to grid.

- Test the Full Controller Without Power Stage

For software integration testing, keep GPIO_LOGIC_TEST_IGNORE_BACKUP_LOW set to True in app_config/settings.py. Then run:

cd /home/justin/Documents/apro-controller-rev2 python3 -m src.main

Unplug the grid sensing input to simulate an outage. The controller should detect grid loss, start the inverter process, switch the relay to backup, and log the software transfer time. Restore grid voltage and confirm it returns to grid mode.

- Test With MOSFET Gates Connected

After the GPIO-only tests are correct, connect the MOSFET gate drive wiring with the transformer still disconnected. Use the inline fuse and current-limited supply. Watch DC current and MOSFET temperature. The H-bridge should not pull high current with no transformer connected.

- Test With Transformer Connected

Connect the transformer with no load first. Transformer inrush may be higher than the steady-state current, so current-limit behavior is usually better than a sensitive OCP latch during controlled bench testing. Do not keep increasing current limit if current stays high instead of settling.

- Add Load Gradually

- Start with no load and verify output voltage.

- Try a small load such as a 35 W fan before testing larger 100-Watt incandescent loads.

- Watch backup voltage, backup current, DC supply current, MOSFET temperature, and transformer temperature.

- Incandescent bulbs can have high cold-filament inrush and may trip protection even when steady-state load is reasonable.

- Logs and Test Evidence

Each run creates a timestamped log file in the logs folder. These logs are useful because they show mode, voltage, current, relay status, inverter status, outage timing, and restore timing.

Example Log File

ls logs

Useful log entries to look for:

[TIMING] Outage timer started [TIMING] SOFTWARE TRANSFER TIME = ... seconds [TIMING] Restore timer started [TIMING] SOFTWARE RESTORE TIME = ... seconds

- Calibration Tuning

K_GRID_V = 1055.5671

K_BACKUP_V = 1055.5671

All calibration values are in app_config/settings.py. Tune only one factor at a time and compare against a trusted meter.

K_GRID_I = 2.9904 K_BACKUP_I = 3.19667

Use this formula when adjusting a scale factor:

new_factor = old_factor * meter_reading / pi_reading

Example: if the Pi reads 0.70 A and the clamp meter reads 0.80 A, use:

new_factor = old_factor * 0.80 / 0.70

- Final Protection Setting

When the backup voltage sensing is connected and protection testing is ready, change this setting in app_config/settings.py:

GPIO_LOGIC_TEST_IGNORE_BACKUP_LOW = False

With this set to False, low backup voltage will create a fault instead of being ignored for testing.

Troubleshooting:

| Symptom | Resolution |
| --- | --- |
| LCD not working | Run i2cdetect -y 1 and confirm address 0x27. Check SDA/SCL wiring and contrast pot. |
| ADC import error | Confirm ADS1263.py exists in ADC_DRIVER_PATH or update the path in settings.py. |
| Grid current reads zero | Run python3 -m scripts.current_channel_debug and verify IN1 current changes with load. |
| Inverter waveform stretches | Confirm the inverter is being run from the process-based InverterController. |
| False transfers | Increase GRID_LOW_COUNT_REQUIRED or OUTAGE_CONFIRM_SECONDS. |